SECTION 03 01	30

MAINTENANCE OF CAST-IN-PLACE CONCRETE

*********************************************************************************************

SPECIFIER NOTE: THIS SPECIFICATION INCLUDES SOME OPTIONS AND CHOICES WITHIN THE TEXT. EDIT ACCORDINGLY.

To view non-printing Editor's Notes that provide guidance for editing, click on the Show/Hide button or Press the Ctrl key, Shift key, and the number 8 simultaneously.

*********************************************************************************************

PART 1 – GENERAL

- SUMMARY

  - Section Includes:

Revise paragraph below to suit Project.

    - Maintenance and repair of cast-in-place concrete spalls, cracks and pin-holes to interior, exposed concrete slabs prior to concrete polishing.

  - Related Requirements:

Revise list below to suit Project.

    - Section 01 33 00 –  Submittal Procedures.

    - Section 01 60 00 –  Product Requirements.

    - Section 03 30 00 – Cast-In-Place Concrete.

    - Section 03 35 43 – Polished Concrete Finishing.

- REFERENCES

  - Reference Standards:

    - The date of the standard is that in effect as the date of receipt of bids for the project.

    - ACI 302.1R – Guide to Concrete Floor and Slab Construction.

    - ASTM International (ASTM):

      - D412-Standard Test Methods for Vulcanized Rubber and Thermoplastic Elastomers—Tension.

      - D695- Standard Test Method for Compressive Properties of Rigid Plastics.

      - D882- Standard Test Method for Tensile Properties of Thin Plastic Sheeting.

      - D1308-Standard Test Method for Effect of Household Chemicals on Clear and Pigmented Organic Finishes.

      - D2240-Standard Test Method for Rubber Property—Durometer Hardness.

- SUBMITTALS

  - Product Data: Submit product data sheets for each type of product specified.

  - VOC Certification: Submit certification that products furnished comply with regulations controlling use of volatile organic compounds (VOC).

  - Certificates:

    - Certificates by manufacturer stating that installer is an approved installer and has completed the necessary training.

- QUALITY ASSURANCE

  - Installer Qualifications:

    - Installer to be certified by the manufacturer in the installation of concrete repair material on exposed concrete floors.

    - Installer should have successfully performed a minimum of 5 projects of similar scope and complexity.

    - Installer must use proper equipment to perform work within scope of this project, as recommended by the manufacturer.

- DELIVERY, STORAGE, AND HANDLING

  - Comply with manufacturer's written instructions for minimum and maximum temperature requirements and other conditions for storage.

  - Deliver materials in original containers, with seals unbroken, bearing manufacturer labels indicating brand name and directions for storage.

- FIELD CONDITIONS

  - Environmental Limitations: Do not apply when air and substrate temperatures are outside limits permitted by manufacturer’s written instructions.

  - Do not apply repair material to concrete that does not comply with manufacturer’s published instructions and ACI 302.1R.

    - Do not apply to wet concrete.

    - Allow adequate time for concrete to cure before application of repair material.

  - Close areas to traffic during and after application for time period as recommended in writing by manufacturer.

PART 2 – PRODUCTS

- MANUFACTURER

  - HI-TECH Systems:  1190 N Del Rio Place, Ontario, CA, (800) 454-5530, www.hitechpolyurea.com.

  - Substitutions:  Refer to Section 01 60 00 - Product Requirements.

- MATERIALS

  - Concrete repair filler material:  Two-part, 100 percent solids, rapid-set, high strength, low viscosity concrete repair material shall be:

    - HT-Spall TX3, manufactured by HI-TECH Systems, Ontario, CA, (800) 454-5530, www.hitechpolyurea.com.

    - Subject to compliance with the following requirements:

      - Comply with national, state and district AIM VOC regulations.

      - Shore hardness of at least 67 when tested in accordance to ASTM D2240.

      - Elongation: Minimum 6 to 8 percent when tested in accordance with ASTM D412.

      - Tensile strength: Minimum 4600 psi when tested in accordance with ASTM D412.

      - Compressive Strength: Minimum 3900 psi (Neat) and 4800 psi (SAND) when tested in accordance with ASTM D695.

      - Bond Strength: Minimum 3450 psi when tested in accordance with ASTM D882.

      - Stain Resistance:  Achieve limited or no discoloration when tested in accordance with ASTM D1308.

PART 3 – EXECUTION

- EXAMINIATION

  - Verification of Conditions:

Revise one or both of the authorities having jurisdiction in the subparagraph below.

    - Examine the slab notify the [Architect][Owner] in writing of any deficiencies.

    - Concrete must be sound, clean and free of dust, grease, curing compounds, waxes and other contaminants that would adversely affect the quality or durability of the repair material.

    - Work area must be free of obstructions and other trades.

    - Work shall commence upon acceptance of the project conditions.

- PREPARATION

  - Surface Preparation:

    - Crack and Spall Repair:

      - Run dry-cut, vacuum-equipped saw to cut and clean the concrete cracks and spalls.

      - Cut vertical edge on large spalls a minimum ¼ inch deep around the perimeter.

      - Vacuum the thoroughly and ensure the cracks and spalls are dry and free of debris.

    - Do not proceed until unsatisfactory conditions have been corrected.

- CRACK AND SPALL REPAIR MATERIAL INSTALLATION

  - General: Comply with manufacturer’s written instructions for mixing, dispensing and installation of the of repair material.

  - Apply repair material bottom-up in cracks and spalls.

    - For repairs at a depth greater than ¼ inch:

      - First apply repair material and subsequently add sand into the product. Repeat as necessary until repair material has overfilled repair area.

  - Allow product to cure before grinding, scraping or cutting excess repair material.  Ensure the repair material is flush with finished floor.

- PIN-HOLE REPAIR MATERIAL INSTALLATION

  - General: Comply with manufacturer’s written instructions for mixing, dispensing and installation of the of repair material.

  - Apply repair material to fill pin-holes after initial dry, metal grinding step.

  - Spread repair material with smoother trowels.

  - Allow product to cure before proceeding with dry, diamond grinding polishing process.

- PROTECTION

  - Protect installed repair material for period recommended manufacturer prior to opening floor to foot traffic or vehicular traffic.

END OF SECTION